## Slide 1: Listed Antifreeze for Fire Sprinkler Systems
Lainey Liotta, Sr. Fire Protection Market Manager at Lubrizol
SFPE Central Ohio Chapter Meeting | September 14, 2022

## Slide 2: Topics
Path to listed antifreezes
Components of an antifreeze listing
Antifreeze requirements per NFPA Standards
Commercially available listed antifreezes
freezemaster™ installation & ITM guidance
Resources and training

## Slide 3
NFPA 13 Temperature Map
  The one-day mean temperature is the average of
  temperatures taken each hour over 24
  hours.
  For example, for points along the maroon
  line, the lowest one-day mean
  temperature is -15°F.
  NFPA 13 A.6.4.2
Notes: Let’s talk about where freezemaster antifreeze can be used. NFPA has a temperature map that shoes the one-day mean temperature across North America. The one-day mean temperature is defined as the average of temperatures taken each hour over a 24 hour period… not at one point in time.

## Slide 4: Why Listed Antifreeze?
Life Safety Concern
1997-2010: 5 documented cases from 1997 to 2010 in which it was concluded that antifreeze in the fire sprinkler system caused an explosion, resulting in occupant injuries and even death
October 2002 – Fire in Mommouth Beach, NJ
Flash fire caused by vapors of propylene glycol-water solution interacting with gas fired heaters in an outdoor, enclosed deck/porch area
18 people injured
August 2009
Kitchen fire activated apartment sprinkler system containing glycerin-based antifreeze that ignited the flames and caused an explosion
1 fatality & 3 injured
July 2010 – Fire in Herriman, UT
Child playing with matches set off apartment sprinkler system
Antifreeze containing propylene glycol caused fire to spread quickly
1 child and 1 adult suffered second- and third-degree burns
Notes: First, let’s go over the background of antifreeze for fire sprinkler systems.
Now, think about the antifreezes you are familiar with. Would you smoke a cigarette or light a match while pouring antifreeze into the hood of your car? Absolutely not – because it’s flammable, right?
Well, until the mid-2000s, installers were putting this same type of antifreeze in a fire sprinkler system. And some still are to this day, despite there being 5 documented cases from 1997 to 2010 where it was concluded that the antifreeze in the fire sprinkler system caused an explosion, resulting in occupant injuries and even death.

## Slide 5: Path to Listed Antifreezes
2012
Jan
2019
2010
Aug
2020
Sept
2022
NFPA Issues TIAs for 13, 13R and 13D with respect to antifreeze and limits the use in an effort to prevent further injuries
NFPA announces the results of Fire Protection Research Study into antifreeze
Johnson Controls® launches
Tyco® LFP® Antifreeze
(1st UL-listed antifreeze)
Deadline to replace nonlisted antifreeze with listed solution*
Lubrizol launches freezemaster™ antifreeze
*Per 2014-2020 Editions of NFPA 25

## Slide 6: What’s in a listing?
Characterization Tests
Pour point
Viscosity
Fluid Performance Tests
High ambient temperature stability
Temperature cycling stability
Exposure to Fire Tests
Sprinkler solution supply system
Fire fighting effectiveness:
Specific gravity
pH
Freeze point
Electrical conductivity
Corrosion rate
Pit depth
Exposure to elastomeric materials
Compatibility with organic coatings
Toxicity
Resistance to leakage
Viscosity at temperature limitations
Light Hazard
Storage
Extra hazard and flammable
Residential
Stress
Impact of galvanic action
Ordinary Hazard 1 & 2
The antifreeze shall be formulated in such a manner to demonstrate the ability of the solution to not substantially contribute to the heat release rate of a fire when tested in accordance with the standard
UL 2901 – Covers the requirements for performance on antifreeze solutions for fire sprinkler systems
Unlisted antifreeze poses life safety issues!
Notes: In order to become listed, an antifreeze must pass several rigorous, multi-faceted tests that are part of UL 2901. You should be using a listed antifreeze because it is not only important to be in compliance with NFPA standards, but also because, as I said before, unlisted antifreezes present life safety concerns because they are combustible. This slide shows just some of the rigorous testing that an antifreeze solution has to go through in order to become listed, including characterization tests, fluid performance tests, and exposure to fire tests. Basically, all of this testing combined has to prove that the antifreeze will not substantially contribute to the heat release rate of a fire, that it will not contribute to corrosion in metallic systems, and at which temperatures it will work effectively and safely.

## Slide 7: Listed Antifreeze Nomenclature
  Minimum use temperature
  Lowest usable temperature as provided by UL, including a safety factor for outside influences
  Freeze point
  Temperature at which solution begins to freeze
  Pour point
  Lowest temperature at which solution will flow / remain pourable
  Burst point
  Temperature at which frozen solution expands and bursts the vessel
Notes: freezemaster antifreeze has a minimum use temperature of -12 degrees Fahrenheit and a freeze point of -15 degrees Fahrenheit. The freeze point is the temperature at which the antifreeze solution begins to freeze. You may notice that unlisted antifreezes do not have a minimum use temperature on them, only a freeze point. That’s because minimum use temperature is a term that UL made up specifically for listed antifreezes. It is the freeze point plus a safety factor for outside influences.
The pour point and the burst point are less commonly referenced, but the pour point is the lowest temperature at which the antifreeze will remain pourable. The burst point is the temperature at which the frozen antifreeze expands so much that it bursts the piping system.

## Slide 8: What To Look Out For In A Listing
  Like sprinkler heads, listings differ amongst listed antifreezes.
  Here are the most common critical differences:
  Minimum use temperature
  System volume limitations
  Minimum pressure requirements
  Compatibility with piping types and other system materials
Notes: A question we frequently get from the field is “What happens if the temperature goes beyond the freeze point?” As long as it doesn’t exceed it’s pour point for a long amount of time, there is nothing you need do to. As it gets warmer, freezemaster will begin to unfreeze and eventually return back to normal. As long as the system isn’t damaged, there is no need to replace the antifreeze. That said, if the temperature drops below the solution’s freeze point, the sprinkler system might not operate as designed, so it’s important to be familiar with the average mean temperatures of your region and adhere to the use parameter’s within freezemaster’s listing.

## Slide 9: Knowledge Assessment #1
  What is the difference between the minimum use temperature
  and freeze point of a listed antifreeze?
  Freeze point is where the solution begins to freeze.
  Minimum use temperature includes a safety factor.
Notes: A question we frequently get from the field is “What happens if the temperature goes beyond the freeze point?” As long as it doesn’t exceed it’s pour point for a long amount of time, there is nothing you need do to. As it gets warmer, freezemaster will begin to unfreeze and eventually return back to normal. As long as the system isn’t damaged, there is no need to replace the antifreeze. That said, if the temperature drops below the solution’s freeze point, the sprinkler system might not operate as designed, so it’s important to be familiar with the average mean temperatures of your region and adhere to the use parameter’s within freezemaster’s listing.

## Slide 10: New Systems: Antifreeze Solution Requirements per NFPA 13
Effective since 2013 Edition
Note: Listed antifreeze solutions are not required to be glycerin or glycol based as long as they pass UL 2901

## Slide 11: Existing Systems: Antifreeze Solution Requirements per NFPA 25 Standards
2014-2020 Editions

## Slide 12: Critical Change
New systems
September 30,
2012
must be installed with a
Existing systems
September 30,
2022
must be drained & refilled
with a listed antifreeze starting:
listed antifreeze starting:
* Effective since the 2013 Edition of NFPA 13. Refer to NFPA standards for specific guidance.
Since the 2013 Edition of NFPA 13…
Per the 2014-2020 Editions of NFPA 25…
Notes: As with any standard and regulation, it’s very detailed, but there are two critically important takeaways. One is since 2012, new antifreeze systems must be installed with a listed antifreeze. Because a listed antifreeze didn’t exist until 2018, many officials made concessions or many contractors employed other freeze protection methods, such as dry systems, up to that point. But now that there are multiple listed antifreezes available on the market, we are seeing these regulations for newly installed systems widely enforced.
The second key takeaway is for existing systems that were installed prior to September 30, 2012. NFPA 25 requires that unlisted antifreeze be drained from these systems and refilled with a listed antifreeze, or employ a different freeze protection method, by September 30, 2022. So, if you are dealing with a system that still uses an unlisted antifreeze, know that it must be replaced with a listed antifreeze or retrofitted with a different freeze protection method by September 30, 2022.

## Slide 13: Existing Systems: Antifreeze Solution Requirements per NFPA 25, 2023 Edition
5.4.4.4
Except as permitted by 5.3.4.4.2 and 5.3.4.4.3, all antifreeze systems shall utilize listed antifreeze solutions
5.3.4.4.1
Where used to replace nonlisted antifreeze solutions, listed antifreeze solutions shall be permitted to be used outside their listing limitations, provided the temperature range limitations are not exceeded
5.3.4.4.2
An existing antifreeze solution shall be permitted to remain in a system, provided the concentrations of the factory premixed antifreeze solution is limited to 30 percent propylene glycol by volume or 38 percent glycerine by volume
5.3.4.4.3
Premixed antifreeze solutions of propylene glycol exceeding 30 percent concentration by volume shall be permitted for use with ESFR sprinklers, provided the ESFR sprinklers are listed for such use in a specific application

## Slide 14: 2023 Edition of NFPA 25 - Annex

## Slide 15: Summary of Changes in 2023 Edition of NFPA 25
Note: NFPA 25 has no retroactivity clause!
Removes September 30, 2022 deadline
  30% propylene glycol by volume or 38% glycerine by volume can remain in system until they test out of temp spec
Permits listed solution usage outside of listing only if replacing nonlisted solution
  Must not exceed temperature range
Permits usage of premixed solutions of PG exceeding 30% concentration with specially listed ESFR sprinklers
Annex lists other considerations:
  Specific gravity & viscosity
  Volume maximums
  Requirements related to hydraulic design

## Slide 16: Now what? Key Considerations for Antifreeze Solutions
Does it provide adequate freeze protection for the system?
        NFPA Temperature Map
        Minimum use temperature and freeze point
Is it specifically listed and approved for use in the application?
        System volume limitations
        Compatibility with piping system materials and system accessories
        Minimum pressure requirements
How does it contribute to the prevention of corrosion and MIC?
Notes: When choosing an antifreeze for fire sprinkler systems, there are several great options available. When you are evaluating antifreeze brands, be sure to make these 4 considerations.

## Slide 17: freezemaster™ Antifreeze
5 gal purple bucket
55 gal white drum
275 gal white tote
NFPA requires a tag be placed on the riser of an antifreeze system that indicates the antifreeze:
Manufacturer
Type
Brand
Concentration
System volume
Hang tag(s) are provided with each container.
Notes: In 2020, Lubrizol launched UL-listed freezemaster antifreeze. It is available through Viking SupplyNet in 5 gallon buckets, 55 gallon drums, and 275 gallon totes. NFPA standards require that a placard be placed on the riser of an antifreeze system indicating the antifreeze manufacturer, type, brand, concentration, and volume of the system. These tags are shipped with each container of freezemaster™ antifreeze. If you need more, you can print some out at www.freezemaster.com.

## Slide 18: freezemaster™ Antifreeze Technical Information
  Minimum use temperature: -12°F (-24°C)
  Lowest usable temperature as provided by UL, including a safety factor for outside influences
  Freeze point: -15°F (-26°C)
  Temperature at which solution begins to freeze
  Pour point: -22.4°F (30°C)
  Lowest temperature at which solution will flow / remain pourable
  Burst point: -58°F (-50°C)
  Temperature at which frozen solution expands and bursts the vessel
Notes: freezemaster antifreeze has a minimum use temperature of -12 degrees Fahrenheit and a freeze point of -15 degrees Fahrenheit. The freeze point is the temperature at which the antifreeze solution begins to freeze. You may notice that unlisted antifreezes do not have a minimum use temperature on them, only a freeze point. That’s because minimum use temperature is a term that UL made up specifically for listed antifreezes. It is the freeze point plus a safety factor for outside influences.
The pour point and the burst point are less commonly referenced, but the pour point is the lowest temperature at which the antifreeze will remain pourable. The burst point is the temperature at which the frozen antifreeze expands so much that it bursts the piping system.

## Slide 19: freezemaster™ Key Attributes
  UL-listed, factory premixed antifreeze that meets NFPA requirements
  Remains in a protective liquid state down to -12°F (-24°C)
  The highest volume allowances for Ordinary Hazard I & II
  The only antifreeze listed for use with galvanized pipe
  Effectively reduces metallic pipe corrosion by up to 65%
  Colored blue so contractors can see the material as it exits the vents and drains when flushing
  and filling systems during the fill process
Notes: Now that we’ve reviewed where freezemaster can be used, we’re going to go over in detail the many benefits of freezemaster antifreeze. Not only is freezemaster UL-listed and safe to use, it also has the most flexible system volume allowances of any antifreeze on the market and it’s the only antifreeze listed for use with galvanized pipe. Other benefits outside of its enhanced listings include superior corrosion performance and its blue color, which allows installers to identify a fully flushed or filled system.
We will go over these benefits in detail in the following slides.

## Slide 20
  Major metropolitan areas benefiting from freezemasterTM antifreeze:
  Baltimore
  Boston
  Boise
  Buffalo
  Chicago
  Cleveland
  Detroit
  Denver
  Halifax
  Indianapolis
Temperature Map
  Milwaukee
  New York City
  Omaha
  Philadelphia
  Pittsburgh
  Portland
  Salt Lake City
  Seattle
  Washington, D.C.
  Vancouver
Notes: freezemaster can be used in areas where the lowest mean temperature is -15 degrees Fahrenheit or more. This includes major metropolitan areas like New York City, Boston, Chicago, Omaha, Salt Lake, Vancouver, just to name a few. As you’ll remember, while -15 degrees is where freezemaster starts to freeze, it won’t freeze into a solid until -58 degrees Fahrenheit. So, if one cold winter night it gets down to -16F or even -20F for a few hours, the system should not break or become damaged. As the temperature rises, the antifreeze will unfreeze and return to its normal liquid state and work as normal. You don’t need to drain and refill the system or anything like that; as long as the system was not damaged, you can leave it as-is as. Obviously, you should always use a product in accordance with its listing, including antifreeze. I just want to emphasize that you don’t have to worry if the temperature infrequently goes below freezemaster’s freeze point for a short period of time.

## Slide 21: Ideal Exterior and Interior Applications
  Small walk-in freezers and refrigerators
  Temperate small parking garages
  Small cold storage facilities
  Roof access hatches
  Industrial refrigeration equipment
  Pits in heated buildings
  Surge areas
  The first few heads of a heated parking garage
  Obstruction heads below bay doors
  Tunnels in heated industrial applications
Notes: The freezemaster™ antifreeze minimum use temperature lends itself to exterior use along the east and west coast of the continental U.S. and in areas south of the central U.S. This, however, does not preclude its use in thousands of interior, partially conditioned spaces around the world. You can use freezemaster in conditioned interior spaces with unheated areas that are vulnerable to freezing, like in breezeways, loading bays, small walk-in freezers, etc. You can also use it in systems where pipes are charged with water in the summer and are drained and charged with air pressure in the winter.

## Slide 22: Knowledge Assessment #2
Notes: A question we frequently get from the field is “What happens if the temperature goes beyond the freeze point?” As long as it doesn’t exceed it’s pour point for a long amount of time, there is nothing you need do to. As it gets warmer, freezemaster will begin to unfreeze and eventually return back to normal. As long as the system isn’t damaged, there is no need to replace the antifreeze. That said, if the temperature drops below the solution’s freeze point, the sprinkler system might not operate as designed, so it’s important to be familiar with the average mean temperatures of your region and adhere to the use parameter’s within freezemaster’s listing.

## Slide 23: Extra Protection Against Microbiologically Influenced Corrosion (MIC)
freezemasterTM antifreeze offers corrosion resistance that outperforms
the other listed alternative.
336 hours of third-party DNA testing found only freezemaster™ antifreeze
lacked any sign of continued biofouling from bacterial growth. The
other listed antifreeze showed signs of biofouling.
Notes: Building on its extensive expertise in metallurgy, Lubrizol performed a series of corrosion tests in addition to those required by UL that demonstrated the superior anti-corrosion performance of freezemaster™ antifreeze. The extra protection covers both typical corrosion and a particular form that has been plaguing the fire sprinkler industry known as microbiologically influenced corrosion, or MIC. In an effort to establish freezemaster™ antifreeze’s MIC resistance versus the other commercially available fluid, Lubrizol contracted with one of the world’s leading laboratories in analyzing metallurgical failure and corrosion behavior. A screening test was developed to explore the conditions conducive to MIC. This lab then conducted accelerated testing to simulate flow around suspended carbon steel coupons that had been inoculated with sulfate-reducing bacteria (desulfovibrio vulgaris).
Sulfate-reducing microorganisms are common in anaerobic environments where they aid in the degradation and reliability of the surfaces they inhabit. After 336 hours of this testing, neither solution showed signs of corrosion, but only the freezemaster™ antifreeze, as determined by DNA testing, lacked any sign of continued biofouling from bacterial growth, setting up the conditions for a future problem with MIC.

## Slide 24: Breakthrough Corrosion Protection
freezemasterTM Antifreeze
Tyco® LFP™ Antifreeze
65% Corrosion
0% Corrosion
30 days
7 months
Long Term Storage Testing
IP287 Test
(Modified version)
Notes: This slide shows the results of the testing Lubrizol conducted.
In an accelerated version of IP 287 test, Lubrizol compared the corrosion behavior on cast iron chips placed on filter paper and saturated with freezemaster™ antifreeze or LFP antifreeze. After two hours, the chips were removed, and the filter paper rinsed to expose the area covered by the chips and arrive at a resulting percentage of rust. freezemaster™ antifreeze presented no corrosion while the other commercially available fluid gave rise to 65% rust during the test, indicating inferior corrosion protection.
No corrosion leads to less maintenance and repairs and a longer system lifetime, providing the building owner more confidence as well as cost savings.

## Slide 25: Compatibility
  The following materials are compatible with freezemaster™ antifreeze:
    *Used in valve seals, head adapters, fittings and joints
    **Other listed antifreezes are not listed as compatible
Steel piping
System Accessories*
Butyl rubber
Galvanized piping**
Brass
Stainless steel
Black steel
Bronze
Natural rubber
Nitrile rubber (NBR)
Styrene-butadiene rubber (SBR)
Piping Systems
EPDM
CPVC
PEX
Cast iron
Notes: In terms of compatibility, freezemaster is listed for use with several piping materials, such as CPVC, PEX, steel, brass, stainless steel, black steel, bronze, and cast iron steel. Freezemaster is the ONLY antifreeze that is UL-listed for use with galvanized piping systems. In terms of compatibility with other system components with rubber type seals like valves, couplings, or specialty sprinkler head adapters, freezemaster is UL listed as compatible with EPDM, butyl rubber, natural rubber, NBR, and SBR.

## Slide 26: freezemaster™Antifreeze - System Size Allowances
*Refer to the Installation Guide for design parameters and listing limitations.
The other listed antifreezes are limited to 40 gal in OH I & II
EXCLUSIVE TO FREEZEMASTER
Note that existing systems can be split into several unique systems without using the dry system hydraulic design criteria as long as each system’s volume does not exceed the maximum volume defined in the listing for the occupancy.
Notes: Every listed antifreeze has parameters around system volume per application, but these parameters vary across each brand of antifreeze, so it’s critically important to always refer to the manufacturer’s guidelines for specific listings and allowances.
In NFPA 13D applications, freezemaster is listed for use in systems up to 500 gallons in volume in accordance with NFPA design criteria.
In NFPA 13R applications, which includes corridors, garages for single dwelling units, and compartmented Ordinary Hazard areas less than 500 square feet, freezemaster is listed for use in systems up to 500 gallons in volume in accordance with NFPA 13R design criteria. In areas like attics in NFPA 13R occupancies where NFPA 13 design criteria is required, use the applicable volume limitation for the hazard area for NFPA 13.
In NFPA 13 light hazard applications, freezemaster is listed for use in systems up to 500 gallons. In systems sized 200 gallons and under, NFPA 13 design criteria is used. In system sizes between 200 gallons and 500 gallons, NFPA 13 dry system hydraulic design criteria must be used, where the system hydraulics are designed as a dry system even though the system is filled with antifreeze.
In NFPA 13 ordinary hazard groups 1 & 2 applications, freezemaster is unique in that it has the highest volume allowances for these applications. Tyco LFP and LFP plus are only listed for system sizes up to 40 gallons in ordinary hazard occupancies. freezemaster on the other hand is listed for use in systems sized up to 375 gallons. In ordinary hazard 1 and 2 systems that are over 40 gallons, dry system hydraulic design criteria must be used.
In NFPA 13 storage applications, freezemaster is listed for use in system volumes up to 45 gallons.
Note that existing systems can be split into several unique systems without using the dry system hydraulic design criteria as long as each system’s volume does not exceed the maximum volume defined in the listing for the occupancy.

## Slide 27: Comparison of Listed Antifreezes
*Refer to the manufacturer’s installation documents for specific design criteria
Antifreeze Brand | Minimum Use Temp | Freeze Point Temp | UL-Listed for use with galv pipe? | Ordinary Hazard System I & II Volume Limitation | NFPA 13 Light Hazard System Volume Limitation | NFPA 13R Residential System Volume Limitations | NFPA 13D Residential System Volume Limitations | Minimum Pressure Requirement | Liquid Color | Testing Procedure
freezemaster™ antifreeze | (-12°F) | (-15°F) | Yes | 375 gal | 500 gal | 500 gal | 500 gal | None | Blue | Refractometer
Noble® Eliminator 1330 | (-17° F) | (-20 F) | No | 40 gal | 40 gal | 500 gal | 500 gal | 20 psi below (-13.3F) | Orange | Hydrometer
Tyco® LFP | (-10°F) | (-13°F) | No | 40 gal | 500 gal | 500 gal | 500 gal | None | Clear | Refractometer
Tyco® LFP+ | (-25°F) | (-28.5°F) | No | 40 gal | 500 gal | 500 gal | 500 gal | 20 psi | Clear | Refractometer

## Slide 28: freezemaster™ Installation Guidance
Equipment needed
  Hand or electric pump
  Manual or electronic chemical refractometer (not a food/beverage version)
    Recommend Fischer Scientific (PN 12561346) or Reichert Technologies (PN 13940000)
Do not dilute a listed antifreeze with water or mix it with other antifreezes
  Any dilution or addition of other fluids will change the properties
Switching system from unlisted to listed antifreeze
  Flush system thoroughly and ensure all water is drained before filling it with freezemaster™ per installation instructions

## Slide 29: Maintaining a freezemaster™ System
NFPA 25 requires antifreeze to be tested annually by a qualified inspector to ensure the freeze point is being maintained. If any sample concentration falls outside of the parameters, drain and refill the system.
  Test the antifreeze for composition effectiveness using a refractometer or hydrometer. Recommended products are found in freezemaster™’s Installation Guide.
  Test at the most remote portion and where it interfaces with the wet pipe system.
  For systems over 150 gallons, one additional test point shall be conducted every 100 feet.
Contact local authorities for proper disposal of freezemaster™
  Safety data sheets are found at www.freezemaster.com under “Resources” tab
Notes: Per NFPA 25, all components, systems and antifreeze shall be tested to verify function as per the intervals specified in NFPA 25. The antifreeze shall be tested for composition effectiveness annually at the most remote portion and where it interfaces with the wet pipe system, using a refractometer or a hydrometer. For systems over 150 gallons, one additional test point shall be conducted every 100 feet. If a sample exhibits a concentration outside of the parameters, the system shall be drained and refilled.

## Slide 30: Knowledge Assessment #3
According to freezemaster’s UL-listing, what is the maximum volume of antifreeze permitted in an Ordinary Hazard I or II system?
375 gallons. In systems between 40 and 375 gallons, dry system hydraulic design criteria must be used.

## Slide 31: Resources and Support
Product Information
Product videos
Technical Support
Training presentation
Additional Resources
Hangtag
FAQs
One-on-one support
Sell Sheet
Installation Guide
Safety Data Sheet
Corrosion White Paper
freezemaster.com
AHJ flyer
Technical Data Sheet
NFPA Standards Chart
Promotional items
All resources are available at www.freezemaster.com
Notes: We’ve covered a lot in this training today and we have several more resources available to you such as installation guides, videos, white papers, a FAQ sheet, and more. All of these great resources can be found at www.freezemaster.com.

## Slide 32: Resources and Support
www.freezemaster.com
Notes: All supporting documentation, videos, and even extra system hang tags can be found under the “Resources” tab at www.freezemaster.com

## Slide 33: Key Learnings
  Listed antifreeze meets the most rigorous standards to comply with NFPA requirements.
  Since September 30, 2012 all new systems must be installed with a listed antifreeze.
  Existing systems must be drained and refilled with a listed antifreeze starting September 30, 2022
  per 2014-2020 Editions of NFPA 25
  Listings among antifreezes vary. When choosing a listed antifreeze, it’s critical to consider:
    Minimum use temperature
    System volume limitations
    Minimum pressure requirements
    Compatibility with piping types and other system materials
Notes: Before this module comes to a close, let’s take a moment to go over some key points.

## Slide 34: Thank you!
With the launch of freezemasterTM antifreeze, it has never been easier to
be in full compliance with NFPA requirements. Don’t wait until September
to address existing systems. Act as soon as the next scheduled
appointment for Inspection, Testing and Maintenance (ITM).

## Slide 35
Typical Antifreeze Loop
Notes: Here is a general overview of an antifreeze system loop. Once the sprinkler system activates, freezemasterTM antifreeze immediately discharges from the sprinklers and is followed by water.
ote that while an expansion tank on a freezemaster antifreeze system is not required, Lubrizol highly recommends installing one as it prevents water intrusion into the system, which could potentially damage the system or alter performance. Lubrizol recommends the use of UL=listed Fire-X-Trol and FPPI expansion tanks, which are both available through Viking SupplyNet.
If you choose not to install an expansion tank, it is critical that thermal expansion is considered in your system design. You can refer to NFPA 13 for alternate options.

## Slide 36: Layout and Design
Reference NFPA 13, 13R and 13D for:
Flow rates
Pipe sizing
Sprinkler spacing
Hanging methods
System design
  Consult NFPA requirements and state and local regulations.
  Ensure system meets size limitations outlined by NFPA.
Notes: There are three distinct figures in NFPA 13 describing the layout of an antifreeze system including the importance of conducting a full flow-through test on a backflow device.
Note that the Hydraulic calculations for the use of antifreeze are outlined in NFPA 13 and it is imperative that these guidelines are followed. Both the Hazen Williams and the Darcy-Weisbach equation are outlined in NFPA 13 as design criteria for antifreeze, and the Darcy-Weisbach equation is generally used for systems over 40 gallons.
If you need guidance or have any questions on planning for or designing a freezemaster antifreeze system, please don’t hesitate to reach out to your local Lubrizol representative.